

Fuel Quality Standards (Paraffinic Diesel) Determination 2025

I, Chris Bowen, Minister for Climate Change and Energy, make the following determination.

Dated **16/02/2025**

Chris Bowen

Minister for Climate Change and Energy

Contents

1 Name 1

2 Commencement 1

3 Authority 1

4 Definitions 1

5 Fuel standard for paraffinic diesel 2

1 Name

 This instrument is the *Fuel Quality Standards (Paraffinic Diesel) Determination 2025*.

2 Commencement

 (1) Each provision of this instrument specified in column 1 of the table commences, or is taken to have commenced, in accordance with column 2 of the table. Any other statement in column 2 has effect according to its terms.

| Commencement information |
| --- |
| Column 1 | Column 2 | Column 3 |
| Provisions | Commencement | Date/Details |
| 1. The whole of this instrument | The day after this instrument is registered. |  |

Note: This table relates only to the provisions of this instrument as originally made. It will not be amended to deal with any later amendments of this instrument.

 (2) Any information in column 3 of the table is not part of this instrument. Information may be inserted in this column, or information in it may be edited, in any published version of this instrument.

3 Authority

 This instrument is made under section 21 of the *Fuel Quality Standards Act 2000*.

4 Definitions

Note: A number of expressions used in this instrument are defined in section 4 of the *Fuel Quality Standards Act 2000*, including fuel.

 In this instrument:

***ASTM*** followed by an alphanumeric code means the testing method developed under that code by the standards development organisation called ASTM International.

***biodiesel*** has the same meaning as in the *Fuel Quality Standards (Biodiesel) Determination 2025.*

***conventional diesel*** has the same meaning as in the *Fuel Quality Standards (Conventional Diesel) Determination 2025.*

***EN*** followed by a numeric code means the testing method developed under that code by the European Committee for Standardization.

***IP*** followed by a numeric code means the testing method developed under that code by the chartered professional body called the Energy Institute.

***mg/kg*** means milligrams per kilogram and is equivalent to ‘parts per million’ or ‘ppm’ by mass.

***% m/m*** means per cent mass by mass, and is equivalent to ‘mass %’, ‘% mass’ and ‘weight %’.

***paraffinic diesel***means a fuel that:

 (a) consists of a minimum of 95% paraffinic (alkane) hydrocarbons before any blending with biodiesel; and

 (b) is suitable for use as a substitute for conventional diesel.

***% v/v*** means per cent volume by volume, and is equivalent to ‘volume %’, ‘vol %’ and ‘% vol’.

5 Fuel standard for paraffinic diesel

 (1) In relation to a parameter mentioned in an item of the following table, paraffinic diesel must comply with the specification for that parameter mentioned in that item.

 (2) For subsection (1), compliance with the specification for a parameter is determined by using the testing method for that parameter mentioned in that item of the table.

| Fuel standard for paraffinic diesel |
| --- |
| Item | Parameter | Specification | Testing Method |
| 1 | Ash content | 0.01% m/m maximum | ASTM D482  |
| 2 | Biodiesel | 7.0% v/v maximum | EN 14078 |
| 3 | Carbon residue—10% distillation residue | 0.3% m/m maximum | ASTM D4530 |
| 4 | Conductivity at ambient temperature | For paraffinic diesel held by a terminal or refinery for sale or distribution: 50 pS/m minimum at ambient temperature | ASTM D2624 |
| 5 | Copper strip corrosion—3 h at 50°C | Class 1 | ASTM D130 |
| 6 | Density at 15°C  | 765–810 kg/m³ | ASTM D1298 |
| 7 | Derived cetane number       | 51 minimum | ASTM D6890 |
| 8 | Distillation: (a) % v/v recovered at 250°C; (b) % v/v recovered at 350°C;(c) T95 | (a) for % v/v recovered at 250°C: 65% v/v maximum;(b) for % v/v recovered at 350°C: 85% v/v minimum;(c) for T95: 360°C maximum | ASTM D86 |
| 9 | Filter blocking tendency | 2.0 maximum | IP 387 |
| 10 | Flash point | 61.5°C minimum | ASTM D93  |
| 11 | Kinematic viscosity | 2.0–4.5 mm2/s at 40°C | ASTM D445  |
| 12 | Lubricity | 400 µm maximum | IP 450 |
| 13 | Manganese content | 2.0 mg/kg maximum  | EN 16576  |
| 14 | Oxidation stability for all paraffinic diesel | 2.5 mg/100 mL maximum | ASTM D2274 |
| 15 | Oxidation stability for paraffinic diesel with >2.0 vol% biodiesel | 20.0 hours minimum | EN 15751 |
| 16 | Sulfur content | 10 mg/kg maximum | ASTM D5453 |
| 17 | Total aromatics content | 1.7 % m/m maximum | EN 12916 Procedure B |
| 18 | Total contamination | 24 mg/kg maximum | EN 12662 |
| 19 | Water content | 200 mg/kg maximum  | ASTM D6304 |

 (3) Any biodiesel component of paraffinic diesel must meet the requirements of section 6 of the *Fuel Quality Standards (Biodiesel) Determination 2025*.